PowerWave Analyst

Document 2 of 3 — High Level Overview & Architecture

Revision 2 — Updated data models, signal roles, display mode rules

What Changed in Revision 2 Updated: DisturbanceRecord — added display_mode, bay_names fields. Updated: AnalogueChannel — added bay_name, is_derived fields. Updated: Signal Role Taxonomy — added DC_FIELD_I, DC_FIELD_V, MECH_SPEED, MECH_VALVE, SEQ_RMS. Added: Display mode determination rules (WAVEFORM vs TREND). Added: Bay auto-grouping architecture. Added: Complementary digital channel pair detection.

# 1. Updated Internal Data Model

## 1.1 DisturbanceRecord — Complete Field List

| Field | Type | Description | New in Rev 2 |
| --- | --- | --- | --- |
| station_name | str | Substation or station name from CFG |  |
| device_id | str | IED/recorder device identifier |  |
| start_time | datetime | Absolute start timestamp |  |
| trigger_time | datetime | Absolute trigger timestamp |  |
| trigger_sample | int | Sample index of trigger point |  |
| sample_rate | float | Primary sampling rate in Hz |  |
| nominal_frequency | float | 50.0 or 60.0 Hz only |  |
| display_mode | str | WAVEFORM (≥200Hz) or TREND (<200Hz) — auto-set by parser | YES |
| analogue_channels | list[AnalogueChannel] | All analogue channel objects |  |
| digital_channels | list[DigitalChannel] | All digital/binary channel objects |  |
| bay_names | list[str] | Unique bay names extracted from channel names | YES |
| time_array | np.ndarray float64 | Time in seconds from start — NON-UNIFORM if multi-rate |  |
| source_format | str | COMTRADE_1991/1999/2013/CSV/EXCEL/PMU_CSV |  |
| file_path | Path | Absolute path to source file |  |
| header_text | str | Content of .HDR file if present |  |
| _rms_cache | dict | Pre-computed RMS arrays |  |
| _phasor_cache | dict | Pre-computed phasor arrays |  |

## 1.2 AnalogueChannel — Complete Field List

| Field | Type | Description | New in Rev 2 |
| --- | --- | --- | --- |
| channel_id | int | Sequential channel number from CFG |  |
| name | str | Original channel name from CFG |  |
| phase | str | Phase: A, B, C, N, AB, BC, CA, Pos-seq, or empty |  |
| unit | str | Engineering unit: A, kA, V, kV, MW, MVAr, Hz, RPM, %, etc |  |
| multiplier | float | CFG multiplier A — applied to raw DAT values |  |
| offset | float | CFG offset B — applied after multiplier. May be non-zero. |  |
| primary | float or None | CT/VT primary rated value. None if not in CFG (NARI). |  |
| secondary | float or None | CT/VT secondary rated value. None if not in CFG. |  |
| ps_flag | str | P=primary, S=secondary values stored in DAT. Default S. |  |
| raw_data | np.ndarray float32 | Physical values AFTER scaling (multiplier + offset applied) |  |
| signal_role | str | Role from taxonomy — see Section 1.4 |  |
| role_confidence | str | HIGH / MEDIUM / LOW from auto-detector |  |
| role_confirmed | bool | True once user confirmed via mapping dialog |  |
| bay_name | str | Bay identifier extracted from channel name e.g. SJTC2 | YES |
| is_derived | bool | True if pre-calculated value stored in file (P, Q from BEN32 slow) | YES |
| colour | str | Hex display colour |  |
| visible | bool | Channel visibility state |  |

## 1.3 DigitalChannel — Complete Field List

| Field | Type | Description | New in Rev 2 |
| --- | --- | --- | --- |
| channel_id | int | Sequential channel number |  |
| name | str | Original channel name from CFG |  |
| normal_state | int | Normal state: 0 or 1 |  |
| signal_role | str | DIG_TRIP / DIG_CB / DIG_PICKUP / DIG_AR / DIG_INTERTRIP / DIG_TRIGGER / DIG_GENERIC |  |
| role_confidence | str | HIGH / MEDIUM / LOW |  |
| role_confirmed | bool | True once user confirmed |  |
| bay_name | str | Bay identifier extracted from channel name | YES |
| is_complementary | bool | True if part of an OPEN+CLOSED pair (GCB, FCB) | YES |
| complementary_id | int or None | channel_id of the paired complementary channel | YES |
| visible | bool | Channel visibility state |  |

## 1.4 Complete Signal Role Taxonomy — Rev 2

### Analogue Roles

| Role Code | Description | Phases | Typical Unit | Notes |
| --- | --- | --- | --- | --- |
| V_PHASE | Phase-to-earth voltage | A, B, C | kV | Standard phase voltage from VT |
| V_LINE | Phase-to-phase voltage | AB, BC, CA | kV | Line voltage |
| V_RESIDUAL | Residual/zero sequence voltage | N | kV | 3U0, VN, V0, Ux |
| I_PHASE | Phase current | A, B, C | A or kA | Standard phase current from CT |
| I_EARTH | Earth/neutral current | N | A or kA | IN, I0, 3I0 |
| V1_PMU | Pos sequence voltage (PMU) | Pos-seq | kV | PMU phasor — no raw waveform |
| I1_PMU | Pos sequence current (PMU) | Pos-seq | A or kA | PMU phasor — no raw waveform |
| P_MW | Active power | 3-phase | MW | Pre-calculated or PMU-derived |
| Q_MVAR | Reactive power | 3-phase | MVAR | Pre-calculated or PMU-derived |
| FREQ | System frequency | — | Hz | Zero-crossing or PMU |
| ROCOF | Rate of change of frequency | — | Hz/s | df/dt |
| DC_FIELD_I | Generator field current (DC) | — | A | Non-zero CFG offset. Always positive. |
| DC_FIELD_V | Generator field voltage (DC) | — | V | Non-zero CFG offset. Always positive. |
| MECH_SPEED | Mechanical shaft speed | — | RPM | Non-zero CFG offset. |
| MECH_VALVE | Valve/gate/governor position | — | % | Non-zero CFG offset. |
| SEQ_RMS | Sequence component RMS | pos/neg/zero | kV | Pre-calculated sequence magnitudes |
| ANALOGUE | Generic — unknown | — | any | Fallback — display only, no analysis |

### Digital Roles

| Role Code | Description | Colour | Notes |
| --- | --- | --- | --- |
| DIG_TRIP | Protection trip output | #FF2222 | Main trip, zone trips, differential trips |
| DIG_CB | Circuit breaker/switch status | #FF8800 | Incl. GCB, FCB. Complementary OPEN/CLOSED pairs auto-detected. |
| DIG_PICKUP | Protection pickup/alarm threshold | #FFAA00 | OVER/UNDER elements, fault detection |
| DIG_AR | Auto-reclose | #44AAFF | Attempt, block, lockout, in-progress |
| DIG_INTERTRIP | Teleprotection/breaker-fail | #FF44FF | 50BF, SEND/RECV, direct trip |
| DIG_TRIGGER | External trigger input | #FFFFFF | Record trigger source |
| DIG_GENERIC | Alarm/supervision/comms-fail | #888888 | COMMFAIL, MCB, enable signals |

## 1.5 Display Mode Rules

Auto-determination from Sample Rate WAVEFORM mode (sample_rate ≥ 200 Hz): Render as continuous line. Apply min/max decimation. RMS, phasor, FFT available. TREND mode (sample_rate < 200 Hz): Render as scatter plot (dots, size=4). No decimation. No FFT. X axis label in minutes for long records. Canvas header shows: TREND RECORD — {rate} Hz. DC/mechanical channels (DC_FIELD_I, DC_FIELD_V, MECH_SPEED, MECH_VALVE): ALWAYS render as trend scatter regardless of sample_rate. Mixed merged session: each source renders in its own mode independently on shared time axis.

## 1.6 Bay Auto-Grouping Architecture

BEN32 multi-bay files contain channels from multiple physical bays in one file. The parser extracts bay names and groups channels automatically.

- Analogue channels: bay name = everything before the last space-separated token (e.g. 'SJTC2 VR' → bay='SJTC2')

- Digital channels: bay name found by matching any known bay name anywhere in the string (because digital names are qualifier-first)

- Known bays populated from analogue channels first, then applied to digital channels

- Each bay becomes a named, collapsible group in the channel panel

- Each bay group rendered with a coloured header bar on the merged canvas

- Within a bay group, standard phase colour convention applies (Red/Yellow/Blue for R/Y/B phases)

## 1.7 Complementary Digital Channel Pair Detection

Generator CBs and some protection schemes produce complementary OPEN/CLOSED channel pairs representing one physical state. These must be detected and displayed as a single state bar on the event timeline.

- Detection: two DIG_CB channels with same device base name, one containing OPEN and other CLOSED

- Examples: 'GCB OPEN' + 'GCB CLOSED', 'FCB OPEN' + 'FCB CLOSED'

- Mark both channels with is_complementary=True and store each other's channel_id in complementary_id

- Event timeline renders complementary pairs as one combined state bar, not two separate channels