PowerWave Analyst

Feature Note — Channel Signal Mapping & Type Assignment

Revision 2 — Updated auto-detection rules from real file analysis

What Changed in Revision 2 Added: R/Y/B to A/B/C phase mapping (Malaysian/British convention — BEN32, TNB grid). Added: Chinese I/U naming detection (NARI — Ia/Ib/Ic, Ua/Ub/Uc, 3I0, 3U0, Ux). Added: Six new generator/mechanical signal roles (DC_FIELD_I, DC_FIELD_V, MECH_SPEED, MECH_VALVE, SEQ_RMS). Added: Non-zero offset as a fingerprint for DC/mechanical channel detection (Priority 2). Added: Pre-calculated power channel detection (P_MW, Q_MVAR with is_derived=True). Added: COMMFAIL alarm exception rule — prevents 87L_COMMFAIL being misclassified as DIG_TRIP. Added: Generator CB types (GCB, FCB) to CB detection keywords. Added: Complementary OPEN/CLOSED pair detection and display as single state bar. Added: Bay prefix stripping for BEN32 'BAYNAME SIGNAL' format. Updated: Taxonomy expanded from 12 to 17 analogue roles.

# 1. What Changed — Auto-Detection Engine

## 1.1 New Phase Convention Support

The original auto-detection only handled IEC A/B/C convention. Real BEN32 files from the Malaysian TNB grid use R/Y/B convention. NARI relays use lowercase a/b/c. All three must be detected correctly.

Phase Mapping Table — All Conventions R → Phase A (BEN32, Malaysian TNB, British utilities) Y → Phase B (BEN32, Malaysian TNB, British utilities) B → Phase C (BEN32, Malaysian TNB, British utilities — NOTE: B means Blue=Phase C, not Phase B) A → Phase A (IEC standard — ABB, Siemens, Reyrolle, Toshiba) B → Phase B (IEC standard — context-dependent, see below) C → Phase C (IEC standard) a → Phase A (Chinese IEC — NARI lowercase convention) b → Phase B (Chinese IEC — NARI lowercase convention) c → Phase C (Chinese IEC — NARI lowercase convention) L1 → Phase A (European numeric convention) L2 → Phase B (European numeric convention) L3 → Phase C (European numeric convention) IMPORTANT: 'B' is ambiguous. In R/Y/B context it means Phase C (Blue). In A/B/C context it means Phase B. Resolution: if other channels in same record use VR/VY or IR/IY → R/Y/B context. Use signal code lookup table.

## 1.2 New Priority 2 — Non-Zero Offset as DC Fingerprint

Real BEN32 slow records contain DC and mechanical channels with large non-zero CFG offsets. This is a reliable fingerprint that was not in the original auto-detection engine:

- FIELD CURRENT channel: offset = -1875.0 A  →  DC_FIELD_I  (always positive DC value)

- FIELD VOLTAGE channel: offset = -1350.0 V  →  DC_FIELD_V  (always positive DC value)

- MECH SPEED channel:    offset = -1000.0 RPM → MECH_SPEED  (shaft rotation rate)

- GOVERNOR VALVE channel: offset = -25.0 %   → MECH_VALVE  (valve position 0-100%)

Detection rule: if ch.offset != 0.0, check name keywords to determine which DC/mechanical role applies. This runs as Priority 2 immediately after unit field check.

## 1.3 New Signal Roles Added

Six new roles added to cover generator and mechanical channels found in BEN32 slow records:

- DC_FIELD_I — Generator rotor field current (DC). Unit: A. Non-zero offset. Always positive.

- DC_FIELD_V — Generator rotor field voltage (DC). Unit: V. Non-zero offset. Always positive.

- MECH_SPEED — Mechanical shaft speed. Unit: RPM. Non-zero offset. Nominal ~3000 RPM at 50Hz.

- MECH_VALVE — Valve, gate, or governor position. Unit: %. Non-zero offset. Range 0-100%.

- SEQ_RMS — Pre-calculated sequence component RMS. Unit: kV. Names: 'O SEQ RMS', 'ZERO SEQ'.

All five DC/mechanical roles always render as TREND (scatter plot) regardless of sample rate. Standard electrical analysis (RMS, phasor, FFT) does not apply to these channels.

## 1.4 COMMFAIL Alarm Exception Rule

Critical: COMMFAIL must NEVER be classified as DIG_TRIP Real BEN32 files contain channels named 'SJTC2 87L/1_COMMFAIL' and 'SJTC2 87L/2_COMMFAIL'. The naive rule 'if 87L in name → DIG_TRIP' would misclassify these as protection trip outputs. They are communication failure alarms, not trip outputs. The ALARM EXCEPTION must be checked FIRST before any other digital detection rule: If name contains COMMFAIL, COMM FAIL, COMM_FAIL, _FAIL, FAIL, ALARM, WARNING, MCB, VTS, BI_EN, BI_MCB → assign DIG_GENERIC regardless of any other keywords present → this overrides all TRIP, PICKUP, AR, INTERTRIP rules This rule was validated against real BEN32 KULW_275kV digital channel data.

## 1.5 Generator CB Types Added

BEN32 slow records from generator substations contain GCB (Generator Circuit Breaker) and FCB (Field Circuit Breaker) status channels not present in transmission line records. These must be classified as DIG_CB:

- 'GCB OPEN', 'GCB CLOSED', 'GCB_OPEN', 'GCB_CLOSED'  →  DIG_CB

- 'FCB OPEN', 'FCB CLOSED', 'FCB_OPEN', 'FCB_CLOSED'  →  DIG_CB

GCB and FCB channels come in complementary pairs (OPEN + CLOSED). Detect and display as a single state bar on the event timeline. See Section 1.6.

## 1.6 Complementary Channel Pair Detection

When two DIG_CB channels share the same device base name and one contains OPEN while the other contains CLOSED, they represent one physical state and must be treated as a complementary pair:

- Detection: find DIG_CB pairs where name_A.replace(OPEN,'').strip() == name_B.replace(CLOSED,'').strip()

- Mark both channels: is_complementary=True, store each other's channel_id in complementary_id

- Event timeline: render complementary pair as one combined state bar (0=closed, 1=open)

- Channel panel: show paired channels grouped together with a link icon

## 1.7 Bay Prefix Stripping for BEN32

BEN32 channel names follow the format 'BAYNAME SIGNALCODE' where BAYNAME is the substation bay identifier. The signal code is always the last space-separated token. Bay prefix stripping must be applied before any signal code lookup:

- 'SJTC2 VR'  →  strip 'SJTC2 '  →  look up 'VR'  →  V_PHASE, phase=A

- 'KPAR IY'   →  strip 'KPAR '   →  look up 'IY'  →  I_PHASE, phase=B

- 'PKLG IN'   →  strip 'PKLG '   →  look up 'IN'  →  I_EARTH, phase=N

Digital channel names use the reverse pattern with bay name embedded anywhere in the string. Use fuzzy matching against the set of known bay names extracted from analogue channels.

# 2. Complete Auto-Detection Priority Order (Rev 2)

Rules applied in strict order. First match wins. For digital channels, alarm exception is checked before all other rules.

Analogue Detection — 8 Priority Rules PRIORITY 1: Unit field (kV/V → V_PHASE, kA/A → I_PHASE, Hz → FREQ, MW → P_MW, MVAR → Q_MVAR, RPM → MECH_SPEED, % → MECH_VALVE) PRIORITY 2: Non-zero offset signature (field current/voltage, RPM, valve % — name keyword refines which role) PRIORITY 3: Power channel name patterns (POWER UNIT, R.POWER, ACTIVE POWER, REACTIVE) PRIORITY 4: Frequency channel name patterns (FREQ , FREQUENCY, DF/DT, ROCOF) PRIORITY 5: Sequence RMS name patterns (O SEQ RMS, ZERO SEQ, NEG SEQ, SEQ RMS) PRIORITY 6: Direct signal code lookup table — covers R/Y/B, A/B/C, a/b/c, 3I0, 3U0, Ux (ALL conventions) PRIORITY 7: Pattern matching on full name (regex for I_A, V_B, CURR, VOLT patterns) PRIORITY 8: Magnitude heuristic (max¦data¦ > 1000 → V_PHASE, 0.1 to 50 → I_PHASE) FALLBACK: ANALOGUE role, LOW confidence → mapping dialog required

Digital Detection — Priority Order (Alarm Exception FIRST) ALARM EXCEPTION (check first, overrides everything): COMMFAIL, COMM FAIL, FAIL, ALARM, MCB, VTS, BI_EN → DIG_GENERIC RULE 1: CB keywords → DIG_CB (CB_R, CB_Y, CB_B, GCB, FCB, 52A, 52B) RULE 2: AR keywords → DIG_AR (79AR, AR_ATTEMPTED, AR_LOCKOUT, RECLOSE, LOCKOUT) RULE 3: Intertrip keywords → DIG_INTERTRIP (50BF, SEND, RECV, INTERTRIP, DIRECT TRIP, POTT) RULE 4: Trigger keywords → DIG_TRIGGER (TRIGGER, TRIG, EXT TRIG) RULE 5: Trip keywords → DIG_TRIP (87L, 21ZBU, Op_Z, Op_ROC, SOTF, GENERAL TRIP, Op_ prefix) RULE 6: Pickup keywords → DIG_PICKUP (OVER, UNDER, FD, PICKUP, START, VEBI_) FALLBACK: DIG_GENERIC, LOW confidence

# 3. Mapping Dialog — Unchanged Requirements

The channel mapping dialog requirements are unchanged from Rev 1 FeatureNote Sections 4 and 5. The dialog must:

- Show all channels in a scrollable table with role dropdown, phase dropdown, unit field, confidence badge

- Support bulk assignment via Shift+click / Ctrl+click multi-select

- Save mapping profiles keyed by station_name + device_id for auto-apply on next load

- Show auto-detection suggestions in italic — HIGH confidence pre-ticked, others not

- Apply ALARM EXCEPTION rule in auto-detection — COMMFAIL channels always shown as DIG_GENERIC

- Show non-blocking validation warnings for duplicate phases, incomplete 3-phase sets

- Provide Confirm and Cancel buttons

Trigger conditions for automatic dialog display:

- Any CSV or Excel file — always show (no naming standard)

- COMTRADE where more than 20% of analogue channels are LOW confidence

- PMU CSV where column auto-detection returned None

- User right-clicks channel and selects Reassign Signal Type

Auto-apply conditions (skip dialog):

- All channels detected at HIGH confidence from known vendor format

- File matches a previously saved mapping profile — show banner notification instead