PowerWave Analyst

Supplement — Multi-Source Merging, Time Sync & PMU Data

Revision 2 — Updated with confirmed Malaysian PMU file findings

What Changed in Revision 2 Added: PMU 241 broken timestamp detection and LOW quality flagging. Added: Voltage raw-Volts auto-scaling confirmed from three real PMU files (500kV, 275kV). Added: SGT to UTC timezone conversion confirmed as mandatory for all Malaysian PMU data. Added: Column prefix stripping for UNIT2_ and KAWA1_ naming patterns. Added: Status field interpretation table (00 00 = healthy, 00 80 = quality flag). Added: Same-event alignment example from 15/10/2025 real grid event. Added: BEN32 slow record and PMU data simultaneously recording same event.

# Part A — Confirmed PMU File Structure (Malaysian Grid)

## A.1 Three Real PMU Files — 15 October 2025 Event

All three PMU files confirmed from the same 15 October 2025 Malaysian grid disturbance:

- PMU ID 241 — Station: 500JMJG-U5 (500kV system). Column format: clean — no prefix. Timestamp: BROKEN format '12:00.0' — flag as LOW quality GPS. Cannot use for GPS auto-alignment.

- PMU ID 254 — Station: 275TMGR-U2 (275kV system). Column format: UNIT2_ prefix e.g. 'UNIT2_V1 Magnitude'. Timestamp: correct HH:MM:SS.mmm format.

- PMU ID 571 — Station: 275BAHS-KAWA1 (275kV system). Column format: KAWA1_ prefix e.g. 'KAWA1_V1 Magnitude'. Timestamp: correct HH:MM:SS.mmm format.

## A.2 Voltage Unit Scale — Confirmed from Real Files

Confirmed: All Malaysian PMU exports store voltage in raw Volts, not kV PMU 241: V1 Magnitude = 505,453.9 V → divide by 1000 → 505.5 kV (500kV nominal confirmed) PMU 254: V1 Magnitude = 283,861.8 V → divide by 1000 → 283.9 kV (275kV nominal confirmed) PMU 571: V1 Magnitude = 280,379.3 V → divide by 1000 → 280.4 kV (275kV nominal confirmed) Auto-scale rule: if max(V1_Magnitude) > 1000 → divide by 1000, unit = kV. Validation: station name prefix digits give nominal kV (500, 275, 132, 66, 33). Cross-check: scaled max should be within +20% / -20% of nominal kV.

## A.3 Timezone — Mandatory SGT to UTC Conversion

All Malaysian PMU timestamps are in Singapore Time (SGT = Asia/Singapore = UTC+8). This is confirmed by the column header 'Time (Asia/Singapore)' present in all three real files. Every timestamp must be converted from SGT to UTC before any GPS-based time alignment operation. Use pandas tz_localize('Asia/Singapore').tz_convert('UTC'). Never store PMU timestamps in local time — always convert to UTC on parse.

## A.4 Status Field Interpretation

The Status column contains a hex flag word. Values observed in real files:

- '00 00' — All healthy, no flags. Good quality data.

- '00 80' — One flag set. Likely GPS quality degraded or data validity flag. Flag rows for engineer review.

Implementation: store raw status string in PmuRecord.status_array (string array). Any non-zero value appended to PmuRecord.data_quality_flags list. Visible in measurement panel as quality indicator.

## A.5 Same-Event Multi-Source Alignment — Real Example

Confirmed Real Event — 15 October 2025 Malaysian Grid PMU 571 (275BAHS-KAWA1): starts 16:12:00.000 SGT — good GPS timestamps — USE AS REFERENCE BEN32 slow (JMHE U2): trigger at 16:12:36.967 SGT — good GPS timestamps — absolute offset PMU 241 (500JMJG-U5): broken timestamp — cross-correlate against PMU 571 frequency channel Alignment strategy for this event: 1. PMU 571 = reference source (alignment_quality = CONFIRMED) 2. BEN32 slow = compute absolute offset from GPS start times 3. PMU 241 = cross-correlate ROCOF or frequency channel against PMU 571 frequency 4. Present all three offsets to engineer in MergeManager dialog for confirmation

## A.6 BEN32 Slow + PMU Simultaneous Recording

The BEN32 slow record (JMHE U2, 50Hz trend, 70 seconds) and the PMU records all capture the same 15 October 2025 event. This demonstrates that a single grid disturbance may produce:

- One or more BEN32 fast records (5000Hz, short duration) from protection IEDs

- One or more BEN32 slow records (50Hz, long duration) from substation trend recorders

- Multiple PMU records (50fps phasor data) from network-wide PMU deployment

All of these must be loadable into one MergedSession in PowerWave Analyst and displayed on a shared time axis. This is the core multi-source merging requirement and the primary competitive advantage over existing tools.

# Part B — Architecture (unchanged from Rev 1)

MergedSession, SessionSource, PmuRecord data models — unchanged from Rev 1 Supplement Part B.

Time synchronisation engine 5-stage pipeline — unchanged from Rev 1 Supplement Part B.

Merged canvas rendering design — unchanged from Rev 1 Supplement Part B.

Refer to the original Supplement document for full architectural detail on these sections.

# Part C — Implementation Updates (Rev 2 Additions)

## C.1 Updated PMU Parser Requirements

- Dynamic metadata extraction: scan file line by line until a row starting with 'Date' is found — never hardcode row index 0 or 1

- Column prefix stripping: apply regex '^[A-Z0-9]+_' to strip UNIT2_, KAWA1_, UNIT_, BAY_ etc before keyword matching

- Broken timestamp detection: if time string does not match HH:MM:SS pattern → flag pmu_record.timestamp_quality = 'LOW'

- LOW quality timestamps: disable GPS auto-alignment for this source. Show amber warning banner on canvas header. Set alignment_quality = 'MANUAL' in SessionSource.

- Voltage auto-scaling: if max(V1_Magnitude) > 1000 → divide array by 1000, set unit = 'kV'

- Nominal voltage validation: extract kV from station name prefix, verify scaled voltage within 20% of nominal

- Status field: parse and store as string array. Non-zero values added to data_quality_flags list.

- Report rate estimation: compute median time delta from timestamps, infer rate in fps

Acceptance criteria additions for Rev 2:

- PMU 241 loads without crash despite broken timestamp — timestamp_quality='LOW', amber banner shown on canvas

- PMU 254 V1 Magnitude 283861 V → auto-scaled to 283.9 kV and displayed with unit kV

- PMU 571 column 'KAWA1_V1 Magnitude' correctly detected as v_mag role after KAWA1_ prefix stripped

- Status '00 80' on PMU 254/571 data rows stored in data_quality_flags — visible in measurement panel

- MergedSession with PMU 571 + BEN32 slow from 15/10/2025: time-aligned correctly on shared canvas